{"text_format":"3","workbook":"xlsx","n_sheets":1,"sheets":["开关阀表单"],"not_rendered":{"images":3,"defined_names":3},"read":"whole","date_system":"1900"}

{"sheet":"开关阀表单","index":0,"n_rows":72,"n_cols":31,"rows_kept":72,"merged":[[0,2,0,16],[2,2,6,16],[7,3,7,6],[7,7,7,11],[7,12,7,14],[7,15,8,15],[7,17,7,20],[7,22,7,24],[7,25,7,26],[7,30,8,30],[8,5,8,6],[8,25,8,26],[9,5,9,6],[10,5,10,6],[11,5,11,6],[12,5,12,6],[13,5,13,6],[14,5,14,6],[15,5,15,6],[16,5,16,6],[17,5,17,6],[18,5,18,6],[18,12,18,27],[19,5,19,6],[19,12,19,27],[20,5,20,6],[21,5,21,6],[22,5,22,6],[22,12,22,27],[23,5,23,6],[23,12,23,27],[24,5,24,6],[25,5,25,6],[26,5,26,6],[27,5,27,6],[28,5,28,6],[29,5,29,6],[30,5,30,6],[31,5,31,6],[32,5,32,6],[33,5,33,6],[34,5,34,6],[35,5,35,6],[36,5,36,6],[37,5,37,6],[37,12,37,27],[38,5,38,6],[38,12,38,27],[39,5,39,6],[40,5,40,6],[41,5,41,6],[42,5,42,6],[43,5,43,6],[44,5,44,6],[45,5,45,6],[46,5,46,6],[47,5,47,6],[48,5,48,6],[49,5,49,6],[50,5,50,6],[51,5,51,6],[52,5,52,6],[53,5,53,6],[54,5,54,6],[55,5,55,6],[56,5,56,6],[57,5,57,6],[58,5,58,6],[58,12,58,27],[59,5,59,6],[60,5,60,6],[61,5,61,6],[62,5,62,6],[63,5,63,6],[64,5,64,6],[65,5,65,6],[68,5,68,6],[69,5,69,6],[70,5,70,6],[71,2,71,16]]}
{"$rows_empty":7}
[null,null,"序号  ","设备信息  Equipment Information",{"$nulls":3},"介质信息  Medium Information",{"$nulls":4},"管道 Pipe",null,null,"关断最大压差","背压","阀门  Valve",{"$nulls":3},"执行器","电磁阀 Solenoid Valve",null,null,"限位开关",null,"安装图号","备注","版本 ","关断最大正向压力"]
[{"$nulls":3},"仪表位号","开关阀类型","阀门/执行器/限位开关 型号",null,"介质","浓度","粘度","温度","密度","尺寸","压力","材料",null,"Mpa","类型","连结","尺寸","压力","类型","类型","气源","电压","Limit Switch"]
[{"$nulls":8},"%","cP","℃","kg/m3","DN","MPa",null,"MPa","Back"," ","方式","DN","MPa","Act.",null,"Air","V","功能","类型",{"$nulls":3},"MPa"]
[null,null,"No.","Tag No.","On-Off Valve  Type","Valve/Actuator/Limit Switch Model",null,"Medium","Cont.","Viscosity","Temp.","S.G.","Size","Press.","Material","dP-Close"," Pressure","Type","CO","Size","Press.","Type","Type","Supply ","Volt.","Function","Type","Hook Up","Remark","Rev.","Close"]
[{"$nulls":4},"再生浆车间"]
[null,null,{"$f":"C12+1","v":1},"OV-E310302","气动开关闸阀",null,null,"浆","7",null,"50",null,600,{"v":1,"d":"1.0"},"SS304","0.05","0","Gate","BF",{"$f":"M13","v":600},"1.0","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3",null,null,0.04]
[null,null,{"$f":"C13+1","v":2},"OV-E310402","气动开关闸阀",null,null,"浆","7",null,"50",null,600,{"v":1,"d":"1.0"},"SS304","0.05","0","Gate","BF",{"$f":"M14","v":600},"1.0","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3",null,null,0.04]
[null,null,3,"OV-T310502","气动开关闸阀",null,null,"浆","3.5",null,"50",null,500,{"v":1,"d":"1.0"},"SS304","0.04","0.3","Gate","BF",500,"1.0","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3",null,null,0.035]
[null,null,4,"OV-T310503","气动开关闸阀",null,null,"浆","3.5",null,"50",null,500,{"v":1,"d":"1.0"},"SS304","0.04","0.3","Gate","BF",500,"1.0","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3",null,null,0.035]
[null,null,5,"OV-E310701","气动O型开关球阀",null,null,"白水","0.1",null,"50",null,100,{"v":1,"d":"1.0"},"SS304","0.3",null,"Ball","F",100,"1.6","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3"]
[null,null,6,"OV-P311001","气动O型开关球阀",null,null,"浆","2.3",null,"50",null,350,{"v":1,"d":"1.0"},"SS304","0.4",null,"Ball","F",350,"1.6","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3"]
[null,null,7,"KV1-E311104","气动开关闸阀","设备带",null,"排渣",null,null,"50",null,"随设备带，不采购"]
[null,null,8,"KV2-E311104","气动开关闸阀","设备带",null,"排渣",null,null,"50",null,"随设备带，不采购"]
[null,null,9,"KV3-E311104","气动O型开关球阀",null,null,"清滤液","0.01",null,"30",null,40,{"v":1,"d":"1.0"},"SS304","0.6",null,"Ball","F",40,"1.6","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3"]
[null,null,10,"OV-P410301","气动O型开关球阀",null,null,"浆","3.2",null,"50",null,300,{"v":1,"d":"1.0"},"SS304","0.55",null,"Ball","F",300,"1.6","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3"]
[null,null,11,"KV1-E410404","气动开关闸阀","设备带",null,"排渣",null,null,"50",null,"随设备带，不采购"]
[null,null,12,"KV2-E410404","气动开关闸阀","设备带",null,"排渣",null,null,"50",null,"随设备带，不采购"]
[null,null,13,"KV3-E410404","气动O型开关球阀",null,null,"清滤液","0.01",null,"30",null,40,{"v":1,"d":"1.0"},"SS304","0.6",null,"Ball","F",40,"1.6","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3"]
[null,null,14,"OV-E410405","气动O型开关球阀",null,null,"清滤液","0.01",null,"30",null,80,{"v":1,"d":"1.0"},"SS304","0.6",null,"Ball","F",80,"1.6","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3"]
[null,null,15,"OV-E410406","气动O型开关球阀",null,null,"清滤液","0.01",null,"30",null,80,{"v":1,"d":"1.0"},"SS304","0.6",null,"Ball","F",80,"1.6","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3"]
[null,null,16,"OV-P311502","气动O型开关球阀",null,null,"白水","0.1",null,"50",null,300,{"v":1,"d":"1.0"},"SS304","0.3",null,"Ball","F",300,"1.6","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3"]
[null,null,17,"OV-P311503","气动O型开关球阀",null,null,"白水","0.1",null,"50",null,250,{"v":1,"d":"1.0"},"SS304","0.4",null,"Ball","F",250,"1.6","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3"]
[null,null,18,"OV-P311504","气动O型开关球阀",null,null,"白水","0.1",null,"50",null,150,{"v":1,"d":"1.0"},"SS304","0.4",null,"Ball","F",150,"1.6","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3"]
[null,null,19,"OV-P311602","气动O型开关球阀",null,null,"白水","0.1",null,"50",null,150,{"v":1,"d":"1.0"},"SS304","0.3",null,"Ball","F",150,"1.6","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3"]
[null,null,20,"OV-T311402","气动O型开关球阀",null,null,"白水","0.1",null,"50",null,150,{"v":1,"d":"1.0"},"SS304","0.3",null,"Ball","F",150,"1.6","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3"]
[null,null,21,"OV-T311202","气动开关闸阀",null,null,"浆","2.6",null,"50",null,400,{"v":1,"d":"1.0"},"SS304","0.15","0.5","Gate","BF",400,"1.0","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3",null,null,0.14]
[null,null,22,"OV-T311203","气动O型开关球阀",null,null,"浆","2.3",null,"50",null,300,{"v":1,"d":"1.0"},"SS304","0.2",null,"Ball","F",300,"1.6","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3"]
[null,null,23,"OV-T311204","气动O型开关球阀",null,null,"浆","2.3",null,"50",null,300,{"v":1,"d":"1.0"},"SS304","0.2",null,"Ball","F",300,"1.6","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3"]
[null,null,24,"OV-E311705","气动O型开关球阀",null,null,"轻渣","0.5",null,"50",null,50,{"v":1,"d":"1.0"},"SS304","0.3",null,"Ball","F",50,"1.6","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3"]
[null,null,25,"OV-P311802","气动O型开关球阀",null,null,"白水","0.05",null,"50",null,250,{"v":1,"d":"1.0"},"SS304","0.05",null,"Ball","F",250,"1.6","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3"]
[null,null,26,"KV1-E311906","气动开关闸阀","设备带",null,"排渣",null,null,"50",null,"随设备带，不采购"]
[null,null,27,"KV2-E311906","气动开关闸阀","设备带",null,"排渣",null,null,"50",null,"随设备带，不采购"]
[null,null,28,"KV3-E311906","气动O型开关球阀",null,null,"清滤液","0.01",null,"30",null,40,{"v":1,"d":"1.0"},"SS304","0.5",null,"Ball","F",40,"1.6","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3"]
[null,null,29,"OV-E312101","气动O型开关球阀",null,null,"浆","0.7",null,"50",null,200,{"v":1,"d":"1.0"},"SS304","0.1",null,"Ball","F",200,"1.6","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3"]
[null,null,30,"OV-E312102","气动O型开关球阀",null,null,"浆","0.7",null,"50",null,200,{"v":1,"d":"1.0"},"SS304","0.1",null,"Ball","F",200,"1.6","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3"]
[null,null,31,"OV-E312103","气动O型开关球阀",null,null,"清滤液","0.01",null,"30",null,50,{"v":1,"d":"1.0"},"SS304","0.6",null,"Ball","F",50,"1.6","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3"]
[null,null,32,"OV-E312305","气动O型开关球阀",null,null,"清滤液","0.01",null,"30",null,50,{"v":1,"d":"1.0"},"SS304","0.6",null,"Ball","F",50,"1.6","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3"]
[null,null,33,"OV-E312904","气动O型开关球阀",null,null,"清滤液","0.01",null,"30",null,40,{"v":1,"d":"1.0"},"SS304","0.6",null,"Ball","F",40,"1.6","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3"]
[null,null,34,"OV-E313005","气动O型开关球阀",null,null,"轻渣","0.5",null,"50",null,50,{"v":1,"d":"1.0"},"SS304","0.2",null,"Ball","F",50,"1.6","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3"]
[null,null,35,"OV-E313205","气动O型开关球阀",null,null,"轻渣","0.5",null,"50",null,32,{"v":1,"d":"1.0"},"SS304","0.2",null,"Ball","F",32,"1.6","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3"]
[null,null,36,"OV-E313405","气动O型开关球阀",null,null,"轻渣","0.5",null,"50",null,32,{"v":1,"d":"1.0"},"SS304","0.2",null,"Ball","F",32,"1.6","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3"]
[null,null,37,"OV-T313502","气动开关闸阀",null,null,"浆","5",null,"50",null,350,{"v":1,"d":"1.0"},"SS304","0.2","0.35","Gate","BF",350,"1.0","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3",null,null,0.14]
[null,null,38,"OV-P313604","气动O型开关球阀",null,null,"浆","3.5",null,"50",null,300,1.6,"SS304","1.1",null,"Ball","F",300,"1.6","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3"]
[null,null,39,"OV-P313605","气动O型开关球阀",null,null,"浆","3.5",null,"50",null,300,1.6,"SS304","1.1",null,"Ball","F",300,"1.6","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3"]
[null,null,40,"OV-P313606","气动O型开关球阀",null,null,"浆","3.5",null,"50",null,300,1.6,"SS304","1.1",null,"Ball","F",300,"1.6","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3"]
[null,null,41,"OV-P313607","气动O型开关球阀",null,null,"浆","3.5",null,"50",null,300,1.6,"SS304","1.1",null,"Ball","F",300,"1.6","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3"]
[null,null,42,"OV-T360102","气动O型开关球阀",null,null,"白水","0.1",null,"50",null,200,{"v":1,"d":"1.0"},"SS304","0.3",null,"Ball","F",200,"1.6","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3"]
[null,null,43,"OV-T360103","气动O型开关球阀",null,null,"白水","0.1",null,"50",null,200,{"v":1,"d":"1.0"},"SS304","0.3",null,"Ball","F",200,"1.6","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3"]
[null,null,44,"OV-T360104","气动O型开关球阀",null,null,"白水","0.1",null,"50",null,200,{"v":1,"d":"1.0"},"SS304","0.3",null,"Ball","F",200,"1.6","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3"]
[null,null,45,"OV-T360105","气动O型开关球阀",null,null,"白水","0.1",null,"50",null,200,{"v":1,"d":"1.0"},"SS304","0.3",null,"Ball","F",200,"1.6","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3"]
[null,null,46,"OV-T360106","气动O型开关球阀",null,null,"白水","0.1",null,"50",null,200,{"v":1,"d":"1.0"},"SS304","0.3",null,"Ball","F",200,"1.6","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3"]
[null,null,47,"OV-E360303","气动O型开关球阀",null,null,"排污","1",null,"50",null,"利旧，原OV-E160104，不采购"]
[null,null,48,"OV-T360601","气动O型开关球阀",null,null,"压缩空气",null,null,"25",null,25,{"v":1,"d":"1.0"},"SS304","0.8",null,"Ball","F",25,"1.6","DA","5/2","0.6MPa","24VDC","I","O+C","CECHK-06-3"]
[]
[]
[]
[]
[]
[{"$nulls":4},"注："]
[{"$nulls":4},"1、所有开关阀订货时带配对法兰，螺栓螺母、紧固件。"]
[{"$nulls":4},"2、背压较大的情况，闸板阀宜选用双向密封。"]
[]
[]
[]
[null,null," 竣工图编制人:                             竣工图审查人："]