{"text_format":"3","workbook":"xlsx","n_sheets":1,"sheets":["调节阀表单"],"not_rendered":{"images":3,"defined_names":3},"read":"whole","date_system":"1900"}

{"sheet":"调节阀表单","index":0,"n_rows":52,"n_cols":32,"rows_kept":52,"merged":[[0,2,0,15],[2,2,6,15],[7,3,7,6],[7,7,7,11],[7,12,7,14],[7,15,8,15],[7,16,7,19],[7,22,7,25],[8,5,8,6],[9,5,9,6],[10,5,10,6],[11,5,11,6],[12,5,12,6],[13,5,13,6],[14,5,14,6],[15,5,15,6],[16,5,16,6],[17,5,17,6],[18,5,18,6],[19,5,19,6],[20,5,20,6],[21,5,21,6],[22,5,22,6],[23,5,23,6],[24,5,24,6],[25,5,25,6],[26,5,26,6],[27,5,27,6],[28,5,28,6],[29,5,29,6],[30,5,30,6],[31,5,31,6],[32,5,32,6],[33,5,33,6],[34,5,34,6],[35,5,35,6],[36,5,36,6],[37,5,37,6],[38,5,38,6],[39,5,39,6],[39,12,39,29],[40,5,40,6],[41,5,41,6],[42,5,42,6],[43,5,43,6],[44,5,44,6],[45,5,45,6],[45,12,45,29],[46,5,46,6],[47,5,47,6],[48,5,48,6],[49,5,49,6],[51,2,51,15]]}
{"$rows_empty":7}
[null,null,"序号  ","设备信息  Equipment Information",{"$nulls":3},"介质信息  Medium Information",{"$nulls":4},"管道 Pipe",null,null,"关断最大压差","阀门  Valve",{"$nulls":3},"执行器","定位器","流量 Flow ",{"$nulls":3},"进口","压差","信号","安装图号","备注","版本 "]
[{"$nulls":3},"仪表位号","调节阀类型","阀门/执行器/定位器 型号",null,"介质","浓度","粘度","温度","密度","尺寸","压力","材料",null,"类型","连结","尺寸","压力","类型","类型","最小","常用","最大","单位","压力"]
[{"$nulls":8},"%","cP","℃","kg/m3","DN","MPa",null,"MPa"," ","方式","DN","MPa","Act.","Posit.",{"$nulls":4},"MPa","MPa","mA"]
[null,null,"No.","Tag No.","Control Valve  Type","Valve/Actuator/Positioner Model",null,"Medium","Cont.","Viscosity","Temp.","S.G.","Size","Press.","Material","dP-Close","Type","CO","Size","Press.","Type","Type","Min.","Nor.","Max.","Unit","P1","DP","Signal","Hook Up","Remark","Rev."]
[{"$nulls":4},"再生浆车间"]
[null,null,{"$f":"C12+1","v":1},"FCV-E310303","气动V型调节球阀",null,null,"白水","0.1",null,"50",null,250,{"v":1,"d":"1.0"},"SS304",{"$f":"AA13+0.2","v":0.5},"BS","F",250,1.6,"DA","PE",0,7000,{"$f":"X13*1.2","v":8400},"l/min","0.3",{"$f":"AA13*0.1","v":{"v":0.03,"d":"0.030"}},"4~20","CECHK-06-1"]
[null,null,{"$f":"C13+1","v":2},"FCV-E310403","气动V型调节球阀",null,null,"白水","0.1",null,"50",null,250,{"v":1,"d":"1.0"},"SS304",{"$f":"AA14+0.2","v":0.5},"BS","F",250,1.6,"DA","PE",0,7000,8400,"l/min","0.3",{"v":0.03,"d":"0.030"},"4~20","CECHK-06-1"]
[null,null,3,"FCV1-T310504","气动V型调节球阀",null,null,"白水","0.1",null,"50",null,125,{"v":1,"d":"1.0"},"SS304",0.5,"BS","BF",100,1.6,"DA","PE",0,1166.5,{"v":1399.8,"d":"1400"},"l/min","0.3",{"v":0.03,"d":"0.030"},"4~20","CECHK-06-1"]
[null,null,4,"FCV2-T310504","气动V型调节球阀",null,null,"白水","0.1",null,"50",null,125,{"v":1,"d":"1.0"},"SS304",0.5,"BS","BF",100,1.6,"DA","PE",0,1166.5,{"v":1399.8,"d":"1400"},"l/min","0.3",{"v":0.03,"d":"0.030"},"4~20","CECHK-06-1"]
[null,null,5,"FCV3-T310504","气动V型调节球阀",null,null,"白水","0.1",null,"50",null,250,{"v":1,"d":"1.0"},"SS304",0.5,"BS","F",200,1.6,"DA","PE",0,7000,8400,"l/min","0.3",{"$f":"AA17*0.1","v":{"v":0.03,"d":"0.030"}},"4~20","CECHK-06-1"]
[null,null,6,"QCV-P311002","气动V型调节球阀",null,null,"白水","0.1",null,"50",null,125,{"v":1,"d":"1.0"},"SS304",0.5,"BS","BF",100,1.6,"DA","PE",0,1625,1950,"l/min","0.3",{"v":0.03,"d":"0.030"},"4~20","CECHK-06-1"]
[null,null,7,"LCV-E410201","气动V型调节球阀",null,null,"白水","0.1",null,"50",null,200,{"v":1,"d":"1.0"},"SS304",0.5,"BS","BF",150,1.6,"DA","PE",0,3498,{"v":4197.6,"d":"4198"},"l/min","0.3",{"v":0.03,"d":"0.030"},"4~20","CECHK-06-1"]
[null,null,8,"QCV-P410302","气动V型调节球阀",null,null,"白水","0.1",null,"50",null,125,{"v":1,"d":"1.0"},"SS304",0.5,"BS","BF",125,1.6,"DA","PE",0,2083,{"v":2499.6,"d":"2500"},"l/min","0.3",{"v":0.03,"d":"0.030"},"4~20","CECHK-06-1"]
[null,null,9,"PCV-E410402","气动V型调节球阀",null,null,"浆","3.19",null,"50",null,200,{"v":1,"d":"1.0"},"SS304",0.5,"BS","BF",150,1.6,"DA","PE",0,{"$f":"5768*0.15","v":{"v":865.2,"d":"865"}},{"$f":"5768*0.5","v":2884},"l/min","0.3",{"v":0.03,"d":"0.030"},"4~20","CECHK-06-1"]
[null,null,10,"LCV-T311401","气动V型调节球阀",null,null,"白水","0.1",null,"50",null,250,{"v":1,"d":"1.0"},"SS304",0.3,"BS","F",{"$f":"M22","v":250},1.6,"DA","PE",0,9500,{"$f":"X22*1.1","v":10450},"l/min","0.1",{"v":0.01,"d":"0.010"},"4~20","CECHK-06-1"]
[null,null,11,"QCV-P311301","气动V型调节球阀",null,null,"白水","0.1",null,"50",null,125,{"v":1,"d":"1.0"},"SS304",0.5,"BS","BF",125,1.6,"DA","PE",0,2264,{"$f":"X23*1.1","v":{"v":2490.4,"d":"2490"}},"l/min","0.3",{"v":0.03,"d":"0.030"},"4~20","CECHK-06-1"]
[null,null,12,"FCV-E311704","气动V型调节球阀",null,null,"浆","2.09",null,"50",null,300,{"v":1,"d":"1.0"},"SS304",0.5,"BS","F",300,1.6,"DA","PE",0,7850,{"$f":"X24*1.2","v":9420},"l/min","0.30",{"v":0.03,"d":"0.030"},"4~20","CECHK-06-1"]
[null,null,13,"FCV-E311706","气动V型调节球阀",null,null,"浆","2.99",null,"50",null,200,{"v":1,"d":"1.0"},"SS304",0.5,"BS","BF",150,1.6,"DA","PE",0,2346,{"v":2815.2,"d":"2815"},"l/min","0.30",{"v":0.03,"d":"0.030"},"4~20","CECHK-06-1"]
[null,null,14,"HCV-P311801","气动V型调节球阀",null,null,"浆","2.0",null,"50",null,200,{"v":1,"d":"1.0"},"SS304",0.65,"BS","F",200,1.6,"DA","PE",0,3533,{"v":4239.6,"d":"4240"},"l/min","0.45",{"v":0.03,"d":"0.030"},"4~20","CECHK-06-1"]
[null,null,15,"FCV-E311904","气动V型调节球阀",null,null,"浆","1.83",null,"50",null,150,{"v":1,"d":"1.0"},"SS304",0.6,"BS","BF",150,1.6,"DA","PE",0,2287,{"v":2744.4,"d":"2744"},"l/min","0.40",{"v":0.03,"d":"0.030"},"4~20","CECHK-06-1"]
[null,null,16,"FCV-E311905","气动V型调节球阀",null,null,"浆","2.28",null,"50",null,125,{"v":1,"d":"1.0"},"SS304",0.6,"BS","BF",125,1.6,"DA","PE",0,1209,{"v":1450.8,"d":"1451"},"l/min","0.40",{"v":0.03,"d":"0.030"},"4~20","CECHK-06-1"]
[null,null,17,"HCV-T312001","气动V型调节球阀",null,null,"清滤液","0.01",null,"30",null,80,{"v":1,"d":"1.0"},"SS304",0.7,"BS","BF",80,1.6,"DA","PE",0,700,840,"l/min","0.5",{"v":0.03,"d":"0.030"},"4~20","CECHK-06-1"]
[null,null,18,"HCV-E312505","气动V型调节球阀",null,null,"清滤液","0.01",null,"30",null,100,{"v":1,"d":"1.0"},"SS304",0.7,"BS","BF",100,1.6,"DA","PE",0,1064,{"v":1276.8,"d":"1277"},"l/min","0.5",{"v":0.03,"d":"0.030"},"4~20","CECHK-06-1"]
[null,null,19,"HCV-E312705","气动V型调节球阀",null,null,"清滤液","0.01",null,"30",null,65,{"v":1,"d":"1.0"},"SS304",0.7,"BS","BF",65,1.6,"DA","PE",0,456,{"v":547.2,"d":"547"},"l/min","0.5",{"v":0.03,"d":"0.030"},"4~20","CECHK-06-1"]
[null,null,20,"FCV-E313004","气动V型调节球阀",null,null,"浆","0.91",null,"50",null,350,{"v":1,"d":"1.0"},"SS304",0.4,"BS","F",350,1.6,"DA","PE",0,12629,{"v":15154.8,"d":"15155"},"l/min","0.2",{"v":0.02,"d":"0.020"},"4~20","CECHK-06-1"]
[null,null,21,"FCV-E313006","气动V型调节球阀",null,null,"浆","1.3",null,"50",null,200,{"v":1,"d":"1.0"},"SS304",0.4,"BS","F",200,1.6,"DA","PE",0,3789,{"v":4546.8,"d":"4547"},"l/min","0.2",{"v":0.02,"d":"0.020"},"4~20","CECHK-06-1"]
[null,null,22,"FCV-E313204","气动V型调节球阀",null,null,"浆","0.76",null,"50",null,250,{"v":1,"d":"1.0"},"SS304",0.45,"BS","F",200,1.6,"DA","PE",0,5154,{"v":6184.8,"d":"6185"},"l/min","0.25",0.025,"4~20","CECHK-06-1"]
[null,null,23,"FCV-E313206","气动V型调节球阀",null,null,"浆","1.35",null,"50",null,125,{"v":1,"d":"1.0"},"SS304",0.45,"BS","BF",125,1.6,"DA","PE",0,1569,{"v":1882.8,"d":"1883"},"l/min","0.25",0.025,"4~20","CECHK-06-1"]
[null,null,24,"FCV-E313404","气动V型调节球阀",null,null,"浆","0.48",null,"50",null,150,{"v":1,"d":"1.0"},"SS304",0.45,"BS","BF",150,1.6,"DA","PE",0,2259,{"v":2710.8,"d":"2711"},"l/min","0.25",0.025,"4~20","CECHK-06-1"]
[null,null,25,"FCV1-E313406","气动V型调节球阀",null,null,"浆","1.26",null,"50",null,125,{"v":1,"d":"1.0"},"SS304",0.45,"BS","BF",80,1.6,"DA","PE",0,869,{"v":1042.8,"d":"1043"},"l/min","0.25",0.025,"4~20","CECHK-06-1"]
[null,null,26,"FCV2-E313406","气动V型调节球阀",null,null,"浆","1.26",null,"50",null,125,{"v":1,"d":"1.0"},"SS304",0.45,"BS","BF",80,1.6,"DA","PE",0,869,{"v":1042.8,"d":"1043"},"l/min","0.25",0.025,"4~20","CECHK-06-1"]
[null,null,27,"QCV-P313602","气动V型调节球阀",null,null,"清滤液","0.01",null,"30",null,80,{"v":1,"d":"1.0"},"SS304",0.49,"BS","BF",80,1.6,"DA","PE",0,700,1190,"l/min","0.29",0.029,"4~20","CECHK-06-1"]
[null,null,28,"FCV-P313603","气动V型调节球阀",null,null,"浆","3.5",null,"50",null,"利旧、原FCV-P143213，不采购"]
[null,null,29,"FCV-P313608","气动V型调节球阀",null,null,"浆","3.5",null,"50",null,200,1.6,"SS304",0.6,"BS","BF",150,1.6,"DA","PE",0,1736,1984,"l/min","0.4",{"v":0.03,"d":"0.030"},"4~20","CECHK-06-1"]
[null,null,30,"FCV-P313609","气动V型调节球阀",null,null,"浆","3.5",null,"50",null,200,1.6,"SS304",0.6,"BS","BF",150,1.6,"DA","PE",0,1736,1984,"l/min","0.4",{"v":0.03,"d":"0.030"},"4~20","CECHK-06-1"]
[null,null,31,"FCV-P313610","气动V型调节球阀",null,null,"浆","3.5",null,"50",null,200,1.6,"SS304",0.6,"BS","BF",150,1.6,"DA","PE",0,1736,1984,"l/min","0.4",{"v":0.03,"d":"0.030"},"4~20","CECHK-06-1"]
[null,null,32,"FCV-P313611","气动V型调节球阀",null,null,"浆","3.5",null,"50",null,200,1.6,"SS304",0.6,"BS","BF",150,1.6,"DA","PE",0,1736,1984,"l/min","0.4",{"v":0.03,"d":"0.030"},"4~20","CECHK-06-1"]
[null,null,33,"FCV-P313612","气动V型调节球阀",null,null,"浆","3.5",null,"50",null,200,1.6,"SS304",0.6,"BS","BF",150,1.6,"DA","PE",0,1736,1984,"l/min","0.4",{"v":0.03,"d":"0.030"},"4~20","CECHK-06-1"]
[null,null,34,"LCV-E360302","气动V型调节球阀",null,null,"清滤液","0.01",null,"30",null,"利旧，原LCV-E160103，不采购"]
[null,null,35,"LCV1-T360701","气动V型调节球阀",null,null,"清水",null,null,"25",null,150,{"v":1,"d":"1.0"},"SS304",0.6,"BS","BF",150,1.6,"DA","PE",0,3000,4000,"l/min","0.4",{"v":0.04,"d":"0.040"},"4~20","CECHK-06-1"]
[null,null,36,"LCV2-T360701","气动V型调节球阀",null,null,"清滤液","0.01",null,"30",null,100,{"v":1,"d":"1.0"},"SS304",0.5,"BS","BF",80,1.6,"DA","PE",0,1154,1500,"l/min","0.3",{"v":0.03,"d":"0.030"},"4~20","CECHK-06-1"]
[]
[{"$nulls":4},"注："]
[{"$nulls":4},"1、所有调节阀订货时带配对法兰，螺栓螺母、紧固件。"]
[null,null," 竣工图编制人:                             竣工图审查人："]